|  | ......................... pcs. .............................. € .............................. € GEZE automatic swing door drive Powerturn F/R Single-leaf, for on-site fire or smoke protection doors, (fire protection approval available), approved hold-open system in accordance with the “General requirements and test principles for the approval of hold-open systems” (DIBt), as a low-noise electromechanical swing door drive for internal and external doors, 70 mm overall height, with hold-open mechanism in accordance with DIN 18263 Part 4, prepared for connection to trigger mechanism, with adjustable spring force EN size 4-7, type-approved and certified in accordance with DIN EN 16005. Product declaration according to LEED and DGNB Reduced effort required for manual opening thanks to the “Smart swing” function (DIN 18040 optimised), release in the event of an alarm by integrated smoke switch under the cover extension of the swing door drive (the smoke switch forms a functional and visual unit with the swing door drive), restoration of operational readiness after alarm activation by switching modes of operation or by opening the door leaf manually, release of the hold-open system with manual trigger switch or by pulling the door leaf closed (manual release), with mounting plate kit - Intelligent digital control (category 2 in accordance with DIN EN 954-1 and Performance Level D in accordance with DIN EN ISO 13849-1). Version: ( ) Optional: with manual trigger switch for releasing the hold-open system ( ) surface- mounted or ( ) flush-mounted ( ) ( ) pushing, transom installation on the opposite hinge side with roller guide rail (EN 4-6) ( ) pushing, transom installation on the opposite hinge side with link arm (EN 6-7) ( ) pulling, transom installation on the hinge side with roller guide rail (EN 4-6) - Functions: - Operating modes: permanently open, automatic, shop closing, night, off adjustable using the integrated programme switch - Low-energy mode (low-energy drive) in accordance with DIN EN 16005, easy manual opening of swing doors from closing position (from 0°) thanks to decoupled power storage device and intelligent evaluation of the sensors, with free swing function for internal doors without load due to wind pressure, door closer operation with torque controlled closing, - obstruction detection and reversing, - diagnosis function and fault memory, - all settings can be made through the display programme switch Technical features: Dimensions: 70 x 130 x 720 mm (H x D x L), mains connection: 230 V AC, 50/60 Hz, door leaf width: min./max. 800/1600 mm, door weight: max. 600 kg fire protection approval up to a door weight of 600 kg Door opening angle: approx. 110°, opening and closing time adjustable, electrical latching action adjustable, hold-open time adjustable from 0 to 60 seconds, contour-controlled opening and closing Connection possibilities: Separate inputs for inner and outer sensors, emergency-stop switch, programme switch, motor lock, on-site door opener, power supply for external devices: 24 V DC, 1200 mA permanently, 1800 mA temporarily Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan, commissioning to be carried out by plant fitters or service partner. - In accordance with DIN EN 16005: - - Safety analysis must be carried out as a basis for planning and execution - - Maintenance and accident prevention (UVV) inspection must be carried out at least 1 x year - - The secondary closing edge of an automatic swing leaf door must be safeguarded - If there is no safeguard, the safety analysis must refer to the residual risk. - Safeguarding of the secondary closing edge is to be carried out on site and is not part of the scope supplied by GEZE GmbH. - We recommend the use of a finger protection screen or round profiles to safeguard the secondary closing edge. Note on locking: Electric strike, for releasing the door, 24 V DC, as a counterpart to the latch lock, as well as lock switch contact to switch off the drive when the door is locked (1 piece per drive) must be provided. Light alloy cover hood in the colour: ( ) anodised EV 1 ( ) RAL ..... |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € FT500—B Compact electric strike for fire protection doors in fail secure version, approved for use on fire protection doors, for all-purpose use right-hand / left-hand with 3 mm adjustable radius latch, latch engagement depth: 6.5 mm with twin coil technology, with bipolar EMC protective diode, retention force: 8000 N Nominal voltage for momentary contact: 12 - 48 V AC/DC Nominal voltage permanent operation: 12 or 24 V AC/DC Current consumption: 100 mA at 24 V VDS Class B Dimensions: 15.8 x 59.5 x 25.5 mm (W x H x D) Without strike plate |
|  | ......................... pcs. .............................. € .............................. € FT501—E Compact electric strike for fire protection doors in fail secure version, with signal processor and power-saving mode, approved for use on fire protection doors, for all-purpose use right-hand / left-hand with 3 mm adjustable radius latch, latch engagement depth: 6.5 mm with bipolar EMC protective diode, retention force: 8000 N Nominal voltage for permanent operation: 8 - 24 V AC/DC Current consumption: 200 mA (with 8 - 11 V) Current consumption: 50 mA (with 12 - 24 V) VDS Class B Dimensions: 15.8 x 59.5 x 25.5 mm (W x H x D) Without strike plate |
|  | ......................... pcs. .............................. € .............................. € Optional position ( ) GEZE lock switch contact for switching off the drive when the door is locked |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GEZE GC 342 laser scanner, tested in accordance with DIN EN 16005, mounted on the door leaf, to protect the swivelling range of interior and exterior doors in the opening and closing direction. Robust enough to handle all floor conditions (e.g. entrance mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating). With integrated wall blanking and dynamic main closing edge protection. Door leaf width: ....... mm ( ) GC 342 laser scanner kit (contains two sensors to protect both sides of the leaf) IP rating IP54, with optimised secondary closing edge protection. If fingers are very likely to be trapped, an additional mechanical solution on the secondary closing edge can be considered. The secondary closing edge protection near the door hinges must be carried out on-site or by the door manufacturer on the basis of the safety analysis. ( ) GC 342 for hinge side and GC 342+ for the opposite hinge side Combination of GC 342, IP rating IP54 for the hinge side and GC 342+, IP rating IP44 for the opposite hinge side. Each as an individual module (left and right variants) Version: ( ) stainless steel colour ( ) black ( ) white ( ) Fire protection kit - master-slave replacement cable which enables cables to be guided through 5 mm instead of 10 mm bore-holes. The drilling permit must be requested from the door manufacturer. Only available for GC 342: Protective cover to protect the laser scanner against interferences ( ) stainless steel colour ( ) black ( ) according to RAL ( ) Retrofit interface - retrofit circuit board for connection to door cables fitted on site |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GEZE safety sensors kit, in sleek narrow strip with IP rating 52, type-approved in accordance with DIN EN 16005, installed on the door leaf, for protecting the door's swivelling range in the opening and closing direction. With integrated wall blanking (kit contains 2 safety sensors for protecting both leaf sides) Door leaf width: ....... mm With asymmetrical double-leaf doors with TSA 160 NT-IS, TSA 160 NT F-IS, EMD-IS, EMD F-IS: Door leaf width, active leaf: ....... mm Door leaf width, passive leaf: ....... mm ( ) GC 338 safety sensor kit for internal and external doors and all floor conditions (e.g. floor mat, metal rail, dark and absorbing flooring, shiny and wet tiles, grating). Version: ( ) EV1 ( ) according to RAL ( ) GC 338 rain cover to protect the safety sensor against interference caused by rain The secondary closing edge protection near the door hinges must be carried out on site or by the door manufacturer on the basis of the safety analysis. GEZE linkage element with integrated sensor, for the space-saving installation of sensor and link arm or guide rail on one plane, tested in accordance with DIN EN 16005, installed on the door leaf Version: ( ) GC GR, with integrated, two-part guide rail profile ( ) Adapter for the integration of the sensor strip with the link arm |
|  | ......................... pcs. .............................. € .............................. € Safeguarding (optional position) GEZE emergency stop switch with glass pane and lighting for switching off the mains voltage, IP rating IP 20 ( ) Surface-mounted ( ) Flush-mounted An emergency command device (emergency stop switch) is not essential for compliance with DIN EN 16005. |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GC 308 radar movement detector with direction detection and cross-traffic fade-out for activation, IP 54 rating, multi-colour LED feedback Dimensions (WxHxD): 120 x 50 x 50 mm Version: ( ) black ( ) white ( ) stainless steel colour ( ) acc. to RAL ( ) outside ( ) inside Accessories: ( ) Ceiling installation kit ( ) Ceiling bracket ( ) exterior: weather hood |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GC 302 radar movement detector with direction detection and cross-traffic fade-out for activation, IP rating IP 54 Dimensions (WxHxD): 176 x 62 x 52 mm Version: ( ) black ( ) acc. to RAL ( ) outside ( ) inside Accessories: ( ) Ceiling installation kit ( ) exterior: weather hood |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GEZE elbow switch, plastic, IP rating IP 30 Dimensions: 90 x 180 x 23 mm ( ) white ( ) stainless steel ( ) optional transmitting module ( ) Surface-mounted ( ) Rear panel for attaching the elbow switch to glass (in connection with the transmitting module) or GEZE elbow switch, LS990, IP rating IP 30 Dimensions: 81 x 223 x 51 mm ( ) white ( ) stainless steel ( ) optional transmitting module ( ) Surface-mounted ( ) Flush-mounted or GEZE elbow switch, stainless steel, IP rating IP 65 Dimensions: 72 x 250 x 17 mm ( ) Surface-mounted or GEZE non-contact proximity switch (radar) Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour. Dimensions: 80 x 80 mm ( ) Flush mounting 12 mm deep ( ) Surface mounting 21 mm deep ( ) Variant for WC or GEZE LED sensor push button, plastic, IP rating IP 69K round, diameter: 100 mm ( ) Flush-mounted ( ) Surface-mounted: mounting ring flat 4 mm ( ) Surface-mounted: mounting ring high 20 mm or GEZE LED sensor push button, glass, IP rating IP 69K round, diameter: 100 mm ( ) Flush-mounted ( ) Surface-mounted: mounting ring flat 4 mm ( ) Surface-mounted: mounting ring high 20 mm or GEZE LED sensor foot switch, glass, IP rating IP69K Dimensions: 100 x 100 x 3 mm ( ) flush-mounting ( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GEZE wireless programme with secure rolling code encryption for wireless activation of the drive (approx. 30 m range in the building). Transmitter: ( ) Hand-held transmitter with 1 key, IP rating IP 54 and wall fixing ( ) Hand-held transmitter with 2 keys, IP rating IP 54 and wall fixing ( ) Hand-held transmitter with 4 keys, IP rating IP 54 and wall fixing ( ) Transmitting module for optional integration in the GEZE elbow switch (not for elbow switch variant stainless steel IP 65) Receiver: ( ) Receiving module with 2 outputs, 24 V, pulse mode or pulse and permanent mode for installation in the drive or in a flush-mounted box with IP rating IP 20 |
|  | ......................... pcs. .............................. € .............................. € Activation (optional position) GEZE GCER 300, 1-door SET Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected. Set comprising: 1 pc. GEZE GCER 300 I/O Box (ID no. 185707) 1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708) 2 pc. GEZE GCER 300 system card master (ID no. 185713) 10 pc. GEZE RFID ID card (ID no. 185711) Optional GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108) GEZE RFID key fob (ID no. 185712) GEZE GCER AP surface-mounted frame (Id. no. 130024) or GEZE GCER 300 Light, 1-door SET Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer. Set comprising: 1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710) 1 pc. GEZE GCER 300 system card master (ID no. 185713) 10 pc. GEZE RFID ID card (ID no. 185711) Optional GEZE RFID key fob (ID no. 185712) GEZE GCER AP surface-mounted frame (ID no. 130024) Accessories for GCER 300 / GCER 300 Light Plug-in power supply NT 1.0 A – 24 V DC (optional) Primary: 230 V AC, 50 Hz Secondary: 24 V DC (+/- 5 %) / 1 A (ID no. 130025) Power supply NT 1.1 A – 24 V DC flush-mounted (optional) For installation in deep standard flush-mounted boxes Primary: 230 V AC, 50 Hz Secondary: 24 V DC / 1.1 A (ID no. 151426) Power supply NT 1.5 A – 24 V DC HA (optional) For installation on top hat rails Primary: 230 V AC, 50 Hz Secondary: 21.6 – 26.4 V DC / 1.5 A (ID no. 151425) |
|  | ......................... pcs. .............................. € .............................. € Opening restrictor (optional position, an opening restrictor is necessary) GEZE door stop, to protect the door and its direct environment. |
|  | ......................... pcs. .............................. € .............................. € Opening restrictor (optional position, an opening restrictor is necessary) GEZE integrated opening restrictor, can also be retrofitted to the guide rail on site. Area of application: internal doors |
|  | ......................... pcs. .............................. € .............................. € - GEZE smoke detector GC 152, 24 V, complete with base, tested in accordance with EN54-7, integrated line monitoring, compliance with DIN EN 14637, can be connected to smoke switch control unit (2 pcs.) - Colour: ( ) white |
|  | ......................... pcs. .............................. € .............................. € - GEZE thermal detector GC 153, 24 V, complete with base, tested in accordance with EN54-5, integrated line monitoring, compliance with DIN EN 14637, can be connected to smoke switch control unit (2 pcs.) - Colour: - ( ) white |
|  | ......................... pcs. .............................. € .............................. € Operation (optional position) GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for commissioning and setting parameters of the drive, with function keys, 2 x 7-segment display, alphanumerical fault display, IP rating IP 40 Operating modes: off, permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted or GEZE mechanical programme switch for setting the operating mode, with rotary button, LED fault display, IP rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert Operating modes: off, permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted or GEZE mechanical programme switch for setting the operating mode, with key, LED fault display, IP rating IP 40, suitable for switch programmes with 55 x 55 mm switch insert Operating modes: off, permanently open, automatic, shop closing, night-locking ( ) Surface-mounted ( ) Flush-mounted |
|  | ......................... pcs. .............................. € .............................. € Operation (optional position) GEZE key switch to “lock” the programme switch to prevent unauthorised changing of the operating mode, IP rating IP 40 ( ) Surface-mounted ( ) Flush-mounted |
|  | ......................... pcs. .............................. € .............................. € CAN interface for the connection to the building management Technical data: CAN interface galvanically isolated. CAN extension module for automatic GEZE sliding door, revolving door and swing door drives as interface to connect to the GEZE building management system myGEZE Control. |
|  | ......................... pcs. .............................. € .............................. € Acceptance test (optional position) Acceptance test for the hold-open system and permanent attachment of the sign of approval |
|  | ......................... pcs. .............................. € .............................. € Building automation connection Building automation and control system For the integration of escape door control units, swing door drives, sliding doors and automatic window systems into a building management system for the use of typical building automation and control functions. An automation controller with the following profile must be used: BACnet device of the type BACnet Building Controller (B-BC) with tested conformity to the BACnet standard ISO 16484-5 myGEZE Control System ...... Piece basic controller as a powerful embedded PC that supports the BACnet protocol. BACnet controller of type B-BC (BACnet Building Controller / protocol audit 14) for the integration of GEZE field bus devices. The number of fieldbus devices is specified in the specifications. The system must be able to provide the following components (incl. software licence): - myGEZE Control basic controller, embedded PC incl. GEZE Library - Terminal system for connecting the GEZE CAN bus - Terminal system for the connection of GEZE window technology based on the IQ box KNX - Terminal system for connecting digital binary input signals to Basis of potential-free contacts - Terminal system for connecting digital output signals based on potential-free door closer or changeover contacts 24 V DC The number of terminal systems is to be determined by the supplier on the basis of the tendered products at field level. In top hat rail housing, incl. power supply unit, required auxiliary terminals for internal potential distribution, bus supply and bus termination. Standard housing dimensions: W x H x D 300 x 400 x 200 mm Supply voltage: 230 V AC incl. the following services: - Project planning and interface configuration of the offered networking system according to GEZE standard. - Mechanical assembly, electrical connection, commissioning ........... Option .............................. € .............................. € Optional additional services: Creation of project-specific wiring schematics for product systems The service includes: - Creation of one basic diagram per door type - Creation of a wiring schematic for the installed door, window and safety technology product systems - A change index is included; additional changes charged separately |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing (option) Service package for maintenance and inspection in accordance with DIN EN 16005, part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years e.g. GEZE compact service package |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package (optional position) Comfort service package for maintenance in accordance with DIN EN 16005, part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to EUR 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - exclusive package (optional position) Exclusive service package for servicing, maintenance in accordance with DIN EN 16005-2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 60 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Complete repair: no separate charging for repairs (parts and working hours) and travel costs during the contract run time - Online access for the client to the project and system data at the contractor’s - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 5 years |